## Chemical Register
4 Parramatta Square (PS4) - Chemical Register
Product Name | Vendor / Manufacturer | Quantity | Location |  |  | MSDS Information | [7 empty] | Consequence | Likelihood | Risk Rating | Safe Work Procedure (SWP) Requirement | Comments/SWP
|  |  |  | U.N. Number (Item 14 of SDS) | HAZCHEM Code (Item 14 of SDS) | GHS Group / Signal Word | SDS Issue Date (DD/MM/YYYY) | Hazardous Substance | Dangerous Good | Hazardous Substance / Dangerous Goods Class | Description | Packing group (Item 14 of SDS) | Subsidiary Risk(s)
Diesel fuel | United Petroleum | 1000 | Level 34 generator room | 3082 | N/A | Danger | 2017-02-23 | Yes | Yes | 9 | Miscellaneous Dangerous Goods | III |  | Moderate | Rare | LOW | SWP is not required | SDS expied. Copy of providers current SDS to be obtained and retained.
360-505CT Cooling Tower Inhibitor | 360 Water | 130 | Level 34 cooling tower zone | 3266 | 2X | Danger | 2020-10-22 | Yes | Yes | 8 | Corrosive | III |  | Moderate | Unlikely | MEDIUM | SWP may be required
360-601BIO Isothiazoline 4% | 360 Water | 130 | Level 34 cooling tower zone | 3265 | 2X | Danger | 2020-10-22 | Yes | Yes | 8 | Corrosive | II |  | Moderate | Unlikely | MEDIUM | SWP may be required
360-52CC Closed Loop Inhibitor | 360 Water | 45 | Level 34 cooling tower zone | 1760 | 2X | Danger | 2020-10-22 | Yes | Yes | 8 | Corrosive | II |  | Moderate | Unlikely | MEDIUM | SWP may be required
BCDMH Tablets (650 BIO) | Redox | 60 | Level 34 cooling tower zone | 3085 | 1W | Danger | 2020-10-22 | Yes | Yes | 5.1 | Oxidising Substances | II | 8 | Moderate | Unlikely | MEDIUM | SWP may be required
Xylene | Omega | 20 | Level 19 plant area | 1307 | 3YE | Danger | 2019-06-30 | Yes | Yes | 3 | Flammable Liquid | III |  | Major | Unlikely | MEDIUM | SWP may be required
ph-7 | Agar | 200 | Level 19 cleaners storage cage | N/A | N/A | Danger | 2021-04-01 | Yes | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
Aqua Clean | The Urinal Shop | 55 | Level 19 cleaners storage cage | N/A | N/A | N/A | 2020-02-01 | No | No |  |  |  |  | Insignificant | Unlikely | LOW | SWP is not required
Body Wash Pearl 3 in 1 | Clean Plus Chemicals (Elyse) | 70 | Level 19 cleaners storage cage | N/A | N/A | N/A | 2021-01-21 | No | No |  |  |  |  | Insignificant | Unlikely | LOW | SWP is not required | No SDS available onsite. Copy of providers SDS to be retained.
Halo Glass Cleaner | Research Products | 25 | Level 19 cleaners storage cage | N/A | N/A | Warning | 2021-09-01 | Yes | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
G-Solve | Agar | 5 | Level 19 cleaners storage cage | N/A | N/A | Danger | 2020-08-01 | Yes | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
Clean Air | Diversey | 30 | Level 19 cleaners storage cage | N/A | N/A | Warning | 2022-12-16 | Yes | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
Exit | Agar | 10 | Level 19 cleaners storage cage | N/A | N/A | Warning | 2020-10-01 | Yes | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
Aqua Foam AQF6011 | Bradley Care | 50 | Level 19 cleaners storage cage | N/A | N/A | Nil | 2020-12-08 | No | No |  |  |  |  | Insignificant | Unlikely | LOW | SWP is not required
Antibacterial Hand Wash (biodegradable) | Central Cleaning Supplies | 230 | Level 19 cleaners storage cage | N/A | N/A | Warning | 2020-03-18 | Yes | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
Go Getter | Diversey | 40 | Level 19 cleaners storage cage | N/A | N/A | Warning | 2021-11-08 | Yes | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
Instant Hand Sanitiser | Clean Plus Chemicals | 15 | Level 19 cleaners storage cage | 1170 | *2Y | Warning | 2020-02-05 | Yes | Yes | 3 | Flammable Goods | II |  | Moderate | Unlikely | MEDIUM | SWP may be required
Tornado | Clean Plus Chemicals | 50 | Level 19 cleaners storage cage | 1760 | 2X | Danger | 2016-09-22 | Yes | Yes | 8 | Corrosive | II |  | Moderate | Unlikely | MEDIUM | SWP may be required | No SDS availab and online copy of providers SDS expired. Current copy of providers SDS to be retained onsite.
Mr Steel | Whitely | 5 | Level 19 cleaners storage cage | N/A | N/A | N/A | 2021-08-01 | No | No |  |  |  |  | Insignificant | Unlikely | LOW | SWP is not required
Lencia | Citrus Resources | 5 | Level 19 cleaners storage cage | N/A | N/A | N/A | 2021-09-01 | No | No |  |  |  |  | Insignificant | Unlikely | LOW | SWP is not required
TASKI Cream R7 | Diversity | 10 | Level 19 cleaners storage cage | N/A | N/A | Warning | 2020-04-14 | Yes | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
Hand Sanitiser Liquid | Sanitiz | 75 | Level 19 cleaners storage cage | 1170 | 2YE | Danger | 2020-08-13 | Yes | Yes | 3 | Flammable Liquid | II |  | Moderate | Unlikely | MEDIUM | SWP may be required
Netbiokem | Callington | 60 | Level 19 cleaners storage cage | N/A | N/A | Warning | 2020-02-04 | Yes | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
Eco Prim Grip | Mapei | 20 | Level 19 maintenance store | N/A | N/A |  | 2022-03-15 | No | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
ID Advanced | Wattyl | 40 | Level 19 maintenance store | N/A | N/A |  | 2020-12-01 | No | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
Nitofill PU150 | Fosroc | 40 | Level 19 maintenance store | N/A | N/A | Danger | 2022-08-09 | Yes | No |  |  |  |  | Moderate | Unlikely | MEDIUM | SWP may be required
Hydro 428 | HydroChem | 15 | Level 19 maintenance store | N/A | N/A | Warning | 2016-05-03 | Yes | No |  |  |  |  | Moderate | Unlikely | MEDIUM | SWP may be required
Enviro 700X | Enviro Systems | 15 | Level 19 maintenance store | N/A | N/A | Danger | 2019-12-31 | Yes | No |  |  |  |  | Moderate | Unlikely | MEDIUM | SWP may be required
K188E | Thomsit | 20 | Level 19 maintenance store | N/A | N/A | Warning | 2022-04-28 | Yes | No |  |  |  |  | Moderate | Unlikely | MEDIUM | SWP may be required
Ultra-Top | Gyprock | 15 | Level 19 maintenance store | N/A | N/A |  | 2023-08-23 | No | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
414 Euroflex Lino Plus | Eurocol | 20 | Level 19 maintenance store | N/A | N/A |  | 2015-08-12 | No | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
Low Odour Solvent | Holdfast | 15 | Level 19 maintenance store | Unknkown | [13 empty] | No data available to assess.
Visocrete 10 | Sika | 10 | Level 19 maintenance store | N/A | N/A |  | 2022-05-23 | No | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
Latex Plus | Mapei | 10 | Level 19 maintenance store | N/A | N/A |  | 2021-03-16 | No | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
Level Pro Finish | Silkafloor | 5 | Level 19 maintenance store | N/A | N/A | Danger | 2020-04-01 | Yes | No |  |  |  |  | Moderate | Unlikely | MEDIUM | SWP may be required
Unknown Liquid |  | 20 | Level 19 maintenance store | [14 empty] | Unknown/unlabelled chemicals should be removed.
Resilient Two Part Polyurethane Adhesive | Regupol | 40 | Level 19 maintenance store | N/A | N/A |  | 2012-07-26 | No | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
One Part Multiuse Flooring Adhesive | Regupol | 20 | Level 19 maintenance store | N/A | N/A |  | 2013-04-17 | No | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
360-57cc Closed Loop Inhibitor | 360 Water | 15 | Level 19 maintenance store | 1760 | 2X | Danger | 2020-10-22 | Yes | Yes | 8 | Corrosive | II |  | Moderate | Unlikely | MEDIUM | SWP may be required
Cover Stain | Zinsser | 4 | Level 19 maintenance store | 1263 | N/A | Warning | 2018-01-25 | Yes | Yes | 3 | Flammable Liquid | III |  | Moderate | Unlikely | MEDIUM | SWP may be required
Core Façade | BC Coating | 10 | Level 19 maintenance store | Unknkown | [13 empty] | No data available to assess.
BC 550 | BC Coating | 20 | Level 19 maintenance store | 1993 | 3YE | Danger | 2022-02-01 | Yes | Yes | 3 | Flammable Liquid | II |  | Moderate | Unlikely | MEDIUM | SWP may be required
Mt Matte | BC Coating | 10 | Level 19 maintenance store | Unknkown | [13 empty] | No data available to assess.
Flash Off | Chempower | 20 | Level 19 maintenance store | N/A | N/A | Warning | 2021-07-31 | Yes | No |  |  |  |  | Moderate | Unlikely | MEDIUM | SWP may be required
Rugasol C | Sika | 10 | Level 19 maintenance store | N/A | N/A |  | 2024-02-22 | No | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
Mastalite | Siniat | 17 | Level 19 maintenance store | N/A | N/A |  | 2021-07-02 | No | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
Water based Paint | Multiple Brands | 200 | Level 19 maintenance store | N/A | N/A |  |  | No | No |  |  |  |  | Insignificant | Rare | LOW | SWP is not required
Methelated Spirits | Diggers | 5 | Level 19 maintenance store | 1170 | 2YE | Danger | 2022-01-31 | Yes | Yes | 3 | Flammable Liquid | II |  | Moderate | Unlikely | MEDIUM | SWP may be required
Mineral Terpentine | Diggers | 6 | Level 19 maintenance store | 1300 | 3Y | Danger |  | Yes | Yes | 3 | Flammable Liquid | III |  | Moderate | Unlikely | MEDIUM | SWP may be required
Bio Activ Drain | Peerless JAL | 5 | Level P2 kitchen cleaner's cupboard | N/A | N/A |  | 2022-02-28 | No | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
Neutral Floor Cleanser | Gleam | 10 | Level P2 kitchen cleaner's cupboard | Unknkown | [13 empty] | No data available to assess.
Handy Andy | Clorox | 5 | Level P2 kitchen cleaner's cupboard | N/A | N/A | Danger | 2021-09-02 | Yes | No |  |  |  |  | Moderate | Unlikely | MEDIUM | SWP may be required
Window and Glass Cleaner | Cleera | 5 | Level P2 kitchen cleaner's cupboard | N/A | N/A | Danger | 2021-04-23 | Yes | No |  |  |  |  | Moderate | Unlikely | MEDIUM | SWP may be required
Methelated Spirits | Glendale | 1 | Level P2 kitchen cleaner's cupboard | 1170 | 2YE | Danger | 2019-06-30 | Yes | Yes | 3 | Flammable Liquid | II |  | Moderate | Unlikely | MEDIUM | SWP may be required
Desaler | Gleam | 5 | Level P2 kitchen cleaner's cupboard | Unknkown | [13 empty] | No data available to assess.
Automatic Dishwashing Liquid | Gleam | 5 | Level P2 kitchen cleaner's cupboard | Unknkown | [13 empty] | No data available to assess.
Aqua Foam AQF6011 | Bradley Care | 5 | Basement 1 cleaners room | N/A | N/A | Nil | 2020-12-08 | No | No |  |  |  |  | Insignificant | Unlikely | LOW | SWP is not required
Hand Sanitiser Liquid | Sanitiz | 5 | Basement 1 cleaners room | 1170 | 2YE | Danger | 2020-08-13 | Yes | Yes | 3 | Flammable Liquid | II |  | Moderate | Unlikely | MEDIUM | SWP may be required
Halo Glass Cleaner | Research Products | 5 | Basement 1 cleaners room | N/A | N/A | Warning | 2021-09-01 | Yes | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
TASKI Cream R7 | Diversey | 5 | Basement 1 cleaners room | N/A | N/A | Warning | 2020-04-14 | Yes | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
Once Off | Agar | 5 | Basement 1 cleaners room | 1719 | 2R | Danger | 2020-08-31 | Yes | Yes | 8 | Corrosive | II |  | Moderate | Unlikely | MEDIUM | SWP may be required
View Quick | Diversey | 5 | Basement 1 cleaners room | N/A | N/A |  | 2023-09-01 | No | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
Cleanair | Diversey | 5 | Basement 1 cleaners room | N/A | N/A | Warning | 2022-12-16 | Yes | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
Go Getter | Diversey | 5 | Basement 1 cleaners room | N/A | N/A | Warning | 2021-11-08 | Yes | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
Mr Steel | Whitely | 5 | Basement 1 cleaners room | N/A | N/A | N/A | 2021-08-01 | No | No |  |  |  |  | Insignificant | Unlikely | LOW | SWP is not required
Dream | Chemrose | 5 | Basement 1 cleaners room | N/A | N/A | Warning | 2022-04-30 | Yes | No |  |  |  |  | Moderate | Unlikely | MEDIUM | SWP may be required
G-Solve | Agar | 1 | Basement 1 cleaners room | N/A | N/A | Danger | 2020-08-01 | Yes | No |  |  |  |  | Minor | Unlikely | LOW | SWP is not required
Hand Sanitiser Gel | Sanitiz | 5 | Basement 1 cleaners room | 1170 | 2YE | Danger | 2020-08-13 | Yes | Yes | 3 | Flammable Liquid | II |  | Moderate | Unlikely | MEDIUM | SWP may be required
Diesel fuel | United Petroleum | 500 | B2 Fire Pump Room (fire pumps x 3) | 3082 | N/A | Danger | 2017-02-23 | Yes | Yes | 9 | Miscellaneous Dangerous Goods | III |  | Moderate | Rare | LOW | SWP is not required | SDS expired. Copy of providers current SDS to be obtained and retained.
Maintain Fricofin LL | Fuchs | 15 | B2 Fire Pump Room | N/A | N/A | Warning | 2015-12-03 | Yes | No |  |  |  |  | Moderate | Unlikely | MEDIUM | SWP may be required
Diesel fuel | United Petroleum | 20000 | B3 Diesel tank room | 3082 | N/A | Danger | 2017-02-23 | Yes | Yes | 9 | Miscellaneous Dangerous Goods | III |  | Moderate | Rare | LOW | SWP is not required | No SDS within room. Copy of providers current SDS to be obtained and retained.
Yes
Volumes
Instructions

## Volumes
Total Volumes of Dangerous Goods
Dangerous Goods Class | Packing Group | Total Quantity | Placarding Required? | Manifest Required? | Fire Protection Quantity?
2.1 - Flammable Gas | - |  | No | No | No
2.2 - Non-Flammable Non-Toxic Gas | - | 0 | No | No | No
2.3 - Toxic Gas | - | 0 | No | No | No
3 - Flammable Liquids | I | 0 | No | No | No
| II | 0 | No | No | No
| III | 30 | No | No | No
4.1 - Flammable Solid | I | 0 | No | No | No
| II | 0 | No | No | No
| III | 0 | No | No | No
4.2 - Spontaneously Combustible | I | 0 | No | No | No
| II | 0 | No | No | No
| III | 0 | No | No | No
4.3 - Dangerous When Wet | I | 0 | No | No | No
| II | 0 | No | No | No
| III | 0 | No | No | No
5.1 - Oxidising Agent | I | 0 | No | No | No
| II | 60 | No | No | No
| III | 0 | No | No | No
5.2 - Organic Peroxide | I | 0 | No | No | No
| II | 0 | No | No | No
| III | 0 | No | No | No
6.1 - Toxic | I | 0 | No | No | No
| II | 0 | No | No | No
| III | 0 | No | No | No
8 - Corrosive | I | 0 | No | No | No
| II | 245 | No | No | No
| III | 130 | No | No | No
9 - Miscellaneous | II | 0 | No | No | No
| III | 21500 | Yes | Yes | Yes
Total Mixed Classes of Dangerous Goods | - | 21965 | Yes | Yes | Yes
Chemical Register
Instructions

## Instructions
Chemical Register Instructions
The Workplace Manager and/or Management OHS Nominee are to ensure that all dangerous goods and hazardous substances stored or handled in the workplace are entered into a Chemical Register and Material Safety Data Sheets are obtained.
The Chemical Register is to be kept up-to-date and reviewed when new chemicals are introduced into the workplace. The Workplace Manager and/or Management OHS Nominee must maintain a hard copy collection of current MSDS (issued within 5 years) from the manufacturer or supplier of all dangerous goods and hazardous substances stored and used in the workplace.
As a minimum, a hard copy of the register along with the appropriate MSDS are to be kept in a central location known to employees.
Where a MSDS has not been provided by the supplier of the product, one may be obtained from the supplier or alternatively from Chemwatch (a link to Chemwatch can be found at the bottom of the home page of the Department's Health, Safety and WorkSafe website).
Risk Assessment and Additional Information
Entering MSDS Details
Entering Quantity and Location
Total Quantities of Dangerous Goods
Changing View and Setting the Print Area
Using the Auto filter
Protected Areas of the Register
Entering Chemical Details
Instructions Introduction
Example Chemical Types
Volumes
Chemical Register

## Instructions 1
Chemical Register Instructions
Entering Chemical Details
Enter the product name and the vendor/manufacturer. It may also be useful to include specific details of the product e.g. 'Ajax Spray and Wipe Citrus Fresh' instead of 'Spray and Wipe', this will help you locate the MSDS.
Risk Assessment and Additional Information
Entering MSDS Details
Entering Quantity and Location
Total Quantities of Dangerous Goods
Changing View and Setting the Print Area
Using the Auto filter
Protected Areas of the Register
Entering Chemical Details
Instructions Introduction
Example Chemical Types
Volumes
Chemical Register

## Instructions 2
Chemical Register Instructions
Entering MSDS Details
You need to review a MSDS for each chemical that is being stored and/or used in the workplace or is being purchased for the first time. This will aid you in determining whether the chemical is a hazardous substance and/or dangerous good and what control measures may be appropriate in order to manage the storage, use and disposal risks of the chemical.
Risk Assessment and Additional Information
Entering MSDS Details
Entering Quantity and Location
Total Quantities of Dangerous Goods
Changing View and Setting the Print Area
Using the Autofilter
Protected Areas of the Register
Entering Chemical Details
Instructions Introduction
Example Chemical Types
Volumes
Chemical Register

## Instructions 3
Chemical Register Instructions
Entering Quantity and Location
Risk Assessment and Additional Information
Entering MSDS Details
Entering Quantity and Location
Total Quantities of Dangerous Goods
Changing View and Setting the Print Area
Using the Autofilter
Protected Areas of the Register
Entering Chemical Details
Instructions Introduction
Example Chemical Types
Volumes
Chemical Register

## Instructions 4
Chemical Register Instructions
Risk Assessment and Additional Information
Dangerous goods and/or hazardous substances are to be assessed to determine the level of risk associated with the storing and usage of these chemicals on site.
Likelihood
Consequence
Risk Matrix
Key
Risk Assessment and Additional Information
Entering MSDS Details
Entering Quantity and Location
Total Quantities of Dangerous Goods
Changing View and Setting the Print Area
Using the Auto filter
Protected Areas of the Register
Entering Chemical Details
Instructions Introduction
Example Chemical Types
Volumes
Chemical Register
Evaluate the likelihood of an incident occurring associated with the use and/or storage of the dangerous good and/or hazardous substance in the workplace.
Evaluate the consequence of the injury associated with the use and/or storage of the dangerous good and/or hazardous substance in the workplace. Reference to the MSDS can be made for details of potential injuries in the use of the dangerous good and/or hazardous substance.
Based on the level of risk (which is automatically determined by finding the intersection between the chosen likelihood and consequence) a SWP is required if the level of risk is identified to be high or extreme.
Enter any supplementary information here such as:
- Specific SWP developed
- Other specific controls (either implemented or yet to be implemented)
- Local policies
- Location of resources e.g. server path
- Ordering/product codes of chemicals
- Information about MSDS availability
- Any other notes/comments
Based on the assessment of the chemical, a SWP may be required. These cells will tell you if:
- A SWP is required;
- SWP may be required as determined on a case by case basis; or
- SWP not required.

## Instructions 5
Chemical Register Instructions
Total Quantities
Based on quantities of dangerous goods entered in the Chemical Register a total quantity summary will automatically highlight whether you need specific legislated controls in the workplace. Should this table indicate that you require placarding, a manifest or fire protection measures, you can contact the WorkSafe Advisory Service on 1800 136 089 for further information.
Risk Assessment and Additional Information
Entering MSDS Details
Entering Quantity and Location
Total Quantities of Dangerous Goods
Changing View and Setting the Print Area
Using the Autofilter
Protected Areas of the Register
Entering Chemical Details
Instructions Introduction
Example Chemical Types
Volumes
Chemical Register
you can contact the WorkSafe Advisory Service on 1800 136 089 for further information.

## Instructions 6
Chemical Register Instructions
Changing View and Setting the Print Area
Risk Assessment and Additional Information
Entering MSDS Details
Entering Quantity and Location
Total Quantities of Dangerous Goods
Changing View and Setting the Print Area
Using the Auto filter
Protected Areas of the Register
Entering Chemical Details
Instructions Introduction
Example Chemical Types
In 'Page Break Preview', once you have entered all applicable chemicals into the Chemical Register, you can move this blue line to set the print area.
If the Register stretches over more that one page, a dashed blue line will represent the page breaks.
Once you select the 'View' tab, you can switch between views here.
You can change the way that you view the worksheet.
Often the best way to work on the sheet is in 'Normal' view but you may need 'Page Break View' to determine what it will look like when printing.
This can be done by selecting the 'View' tab .
Volumes
Chemical Register

## Instructions 7
Chemical Register Instructions
Using the Auto filter
Risk Assessment and Additional Information
Entering MSDS Details
Entering Quantity and Location
Total Quantities of Dangerous Goods
Changing View and Setting the Print Area
Using the Auto filter
Protected Areas of the Register
Entering Chemical Details
Instructions Introduction
Example Chemical Types
These tabs allow you to filter the information entered into the Register. This lets you view only those chemicals that you are interested in at the time e.g. only dangerous goods or only the chemicals in the cleaners cupboard. Remember, you can apply filters to as many of the columns you want.
Once you select a filter arrow, a drop down box will appear. You will be able to select any or all of the categories of information entered into that column. Only items that you have entered somewhere in that column will be available for filtering.
Volumes
Chemical Register

## Instructions 8
Chemical Register Instructions
Protected Areas of the Register
Risk Assessment and Additional Information
Entering MSDS Details
Entering Quantity and Location
Total Quantities of Dangerous Goods
Changing View and Setting the Print Area
Using the Auto filter
Protected Areas of the Register
Entering Chemical Details
Instructions Introduction
Example Chemical Types
To ensure that the formulas in the above columns are not inadvertently deleted, the worksheet has been 'Protected'. If you would like delete a row or sort the data, you will have to unprotect the sheet by selecting the 'Review' tab and clicking 'Unprotect Sheet'.
It is recommended that you do not insert new rows as the required formulas will not be present in the new row.
Once you have finished deleting a row , sorting the data or inserting a row, you should protect the sheet again. This can be done by clicking 'Protect Sheet' (in the 'Review' tab) and selecting 'OK' in the pop-up window.
Volumes
Chemical Register

## Example Chemical Types
Chemical Register Instructions
Example Chemical Register
The following is an example Chemical Register showing multiple chemical types. It demostrates scenarios that you may encounter when developing a Chemical Register for your workplace.
Example Chemical Register
Risk Assessment and Additional Information
Entering MSDS Details
Entering Quantity and Location
Total Quantities of Dangerous Goods
Changing View and Setting the Print Area
Using the Autofilter
Entering Chemical Details
Instructions Introduction
Protected Areas of the Register
Volumes
Chemical Register

## Hide Me (hidden)
Dangerous Goods Class | Packing group | Dangerous Goods Class | Placarding Quantity | Manifest Quantity | Fire Protection Quantity | DG Class | Packaging Group Range Names | Packaging Group Lists Defined |  |  | Workplace Type | Workplace Type Range Names | Primary | Secondary | Office | Camp | Likelihood |  |  | Risk Matrix
3 | I | 2.1 - Flammable Gas | 500 | 5000 | 5000 | N/A | Not_applicable | Not_applicable | List_3 | List_2 | Primary School | Primary | Administration | Administration | Administration | Administration | Descriptor | Level | Definition |  | Consequence
Dangerous Goods Class | Packing group | 2.2 - Non-Flammable Non-Toxic Gas | 2000 | 10000 | 20000 | 1 | Not_applicable | N/A | I | II | Secondary School | Secondary | Staff Room | Staff Room | Kitchen | Kitchen | Rare | Level 1 | May occur, sometime (“once in a life time / once in a hundred years”) | Likelihood | Insignificant | Minor | Moderate | Major | Severe
3 | II | 2.3 - Toxic Gas | 50 | 500 | 2000 | 2.1 | Not_applicable |  | II | III | P-8 College | Secondary | Kitchen | Kitchen | Cleaners | Dormitories | Unlikely | Level 2 | May occur somewhere within DEECD over an extended period of time | Almost Certain | MEDIUM | HIGH | EXTREME | EXTREME | EXTREME
Dangerous Goods Class | Packing group | 3 - Flammable Liquids | 50 | 500 | 2000 | 2.2 | Not_applicable |  | III |  | P-12 College | Secondary | Classrooms | Classrooms | Maintenance | Cleaners | Possible | Level 3 | May occur several times across DEECD or a region over a period of time | Likely | MEDIUM | MEDIUM | HIGH | EXTREME | EXTREME
3 | III |  | 250 | 2500 | 10000 | 2.3 | Not_applicable |  |  |  | Specialist School | Secondary | Cleaners | Cleaners | General/All Areas | Maintenance | Likely | Level 4 | May be anticipated multiple times over a period of time May occur once every few repetitions of the activity or event | Possible | LOW | MEDIUM | MEDIUM | HIGH | EXTREME
Dangerous Goods Class | Packing group |  | 1000 | 10000 | 20000 | 3 | List_3 |  |  |  | Regional/Central Office | Office | Maintenance | Maintenance | Other | Pool | Almost Certain | Level 5 | Prone to occur regularly Is anticipated for each repetition of the activity | Unlikely | LOW | LOW | MEDIUM | MEDIUM | HIGH
4.1 | I | 4.1 - Flammable Solid | 50 | 500 | 2000 | 4.1 | List_3 |  |  |  | Outdoor Education/Camp | Camp | Art Room | Art Room |  | General/All Areas |  |  |  | Rare | LOW | LOW | LOW | MEDIUM | MEDIUM
Dangerous Goods Class | Packing group |  | 250 | 2500 | 10000 | 4.2 | List_3 | [5 empty] | Pool | Science |  | Other | Consequence
4.1 | II |  | 1000 | 10000 | 20000 | 4.3 | List_3 | [5 empty] | General/All Areas | Automotive |  |  | Descriptor | Level | Definition
Dangerous Goods Class | Packing group | 4.2 - Spontaneously Combustible | 50 | 500 | 2000 | 5.1 | List_3 | [5 empty] | Other | Woodwork |  |  | Insignificant | Level 1 | No Injury | Extreme | SWP is required
4.1 | III |  | 250 | 2500 | 10000 | 5.2 | List_3 | [6 empty] | Metalwork |  |  | Minor | Level 2 | Injury/ill health requiring first aid | High | SWP is required
Dangerous Goods Class | Packing group |  | 1000 | 10000 | 20000 | 6.1 | List_3 | [6 empty] | Home Economics |  |  | Moderate | Level 3 | Injury/ill health requiring medical attention | Medium | SWP may be required
4.2 | I | 4.3 - Dangerous When Wet | 50 | 500 | 2000 | 7 | List_3 | [6 empty] | Pool |  |  | Major | Level 4 | Injury/ill health requiring hospital admission | Low | SWP is not required
Dangerous Goods Class | Packing group |  | 250 | 2500 | 10000 | 8 | List_3 | [6 empty] | General/All Areas |  |  | Severe | Level 5 | Fatality
4.2 | II |  | 1000 | 10000 | 20000 | 9 | List_2 | [6 empty] | Other
Dangerous Goods Class | Packing group | 5.1 - Oxidising Agent | 50 | 500 | 2000
4.2 | III |  | 250 | 2500 | 10000
Dangerous Goods Class | Packing group |  | 1000 | 10000 | 20000
4.3 | I | 5.2 - Organic Peroxide | 50 | 500 | 2000
Dangerous Goods Class | Packing group |  | 250 | 2500 | 10000
4.3 | II |  | 1000 | 10000 | 20000
Dangerous Goods Class | Packing group | 6.1 - Toxic | 50 | 500 | 2000
4.3 | III |  | 250 | 2500 | 10000
Dangerous Goods Class | Packing group |  | 1000 | 10000 | 20000
5.1 | I | 8 - Corrosive | 50 | 500 | 2000
Dangerous Goods Class | Packing group |  | 250 | 2500 | 10000
5.1 | II |  | 1000 | 10000 | 20000
Dangerous Goods Class | Packing group | 9 - Miscellaneous Dangerous Goods | 1000 | 10000 | 20000
5.1 | III |  | 5000 | 10000 | 20000
Dangerous Goods Class | Packing group
5.2 | I | Item 4 Mixed Classes of Dangerous Goods | 5000 | 10000 | 20000
Dangerous Goods Class | Packing group
5.2 | II
Dangerous Goods Class | Packing group
5.2 | III
Dangerous Goods Class | Packing group
6.1 | I
Dangerous Goods Class | Packing group
6.1 | II
Dangerous Goods Class | Packing group
6.1 | III
Dangerous Goods Class | Packing group
8 | I
Dangerous Goods Class | Packing group
8 | II
Dangerous Goods Class | Packing group
8 | III
Dangerous Goods Class | Packing group
9 | II
Dangerous Goods Class | Packing group
9 | III